| Utility Services TECHNICAL GUIDE | TG 02500 |
| --- | --- |

1.	COORDINATION ISSUES:  (Not Used)

2.	DESIGN ISSUES:  (Not Used)

3.	DRAWING NOTES:

3.1	Problem/Solution:  To facilitate the detection of non-metallic underground utilities (e.g. PVC, Polyethylene, Polybutylene, Clay, Concrete, etc.), the contract documents shall specify and indicate the provision of a detection wire to be placed over the utility line so that it can be located by use of a metal detector (cable and pipe locator). In addition, a plastic (non-conducting) warning tape shall be provided above the pipe to identify the type of utility service.

3.2	Guidelines:  Therefore, the following guidelines shall be followed:

3.2.1	Detection Wire:

3.2.1.1	Requirement:  Provide for non-metallic underground pipes except for sewer and drain pipes which run directly between manholes and/or inlets and/or headwalls or for other situations where a detection wire will not substantially facilitate detection of the pipe.

3.2.1.2	Material:  Insulated, one-piece (single strand) copper wire, No. 10 ga. (0.1019" dia.) minimum (American or Brown and Sharpe Gage).

3.2.1.3	Location:  The conducting cable shall be buried directly above the center-line of the pipe at a distance of approximately 6" above the top of the pipe. The wire shall extend continuously along the entire length of pipe, from manhole to manhole. The ends of the wire shall terminate inside of each manhole at each end of the pipe, with a minimum of 3' feet of wire, coiled, and remaining accessible in each manhole. The wire shall be insulated along its entire length.

3.2.1.4	Connection:  The coil of wire shall be tied to the gate valve within the manhole. If no gate valve is present, the coil of wire shall be firmly affixed to the manhole side near the manhole cover frame.

3.2.1.5	Splicing:  Where the wires must be joined, the ends shall be tied in a knot and a splice made which provides electrical continuity across the wires.

3.2.2	Warning and Identification Tape:

3.2.2.1	Requirement:  Provide for both non-metallic and metallic underground pipes except for duct banks encased in concrete.

3.2.2.2	Material:  Polyethylene plastic tape, acid and alkali resistant, approximately 3" wide, minimum 0.003" thick, with a strength of 1500 psi lengthwise and 1250 psi crosswise, maximum elongation of 350%, color-coded as noted below, with warning and identification of service imprinted in bold black lettering continuously over the entire length of the tape. Warning and identification to read "CAUTION, BURIED [type of utility service] LINE BELOW" or similar wording. The tape color and printing shall be permanent and unaffected by moisture.

3.2.2.3	Warning Tape Color Codes (Coordinate color codes with applicable sections of the specifications):

Yellow		Electric, Gas, Oil, Dangerous Materials

Orange	Telephone and Communication

Blue		Water

White		Steam

Gray		Compressed Air

3.2.2.4	Location:  The tape shall be buried directly above the center-line of the utility pipe, approximately 12" below finished grade. Where the utility pipe is under pavements and slabs, the tape shall be buried approximately 6" below the top of the subgrade.

4.	STANDARD DRAWINGS:  (Not Used)

5.	SPECIFICATION NOTES:  (Not Used)

6.	GUIDE SPECIFICATION:  (Not Used)

END OF SECTION 02500