| Commissioning of HVAC Systems TECHNICAL GUIDE | TG 15595 |
| --- | --- |

1.	COORDINATION ISSUES:

1.1	Coordinate with Air Conditioning sections and Electrical sections.

2.	DESIGN ISSUES: (Not Used)

3.	DRAWING NOTES: (Not Used)

4.	STANDARD DRAWINGS: (Not Used)

5.	SPECIFICATION NOTES:  (Not Used)

6.	GUIDE SPECIFICATION:

6.1	Section 15595 Commissioning of HVAC Systems.

SPECIFIER’S NOTE:  Blue colored texts are Notes to the Specifier and should be completely deleted from the final text.  Where [red colored italicized text in parentheses] is shown in this specification section, insert wording, numbers, etc. as appropriate and delete parentheses.  Where <Red colored text in brackets> is shown, choice is indicated.  Make the appropriate choice and delete the brackets.  Maintain footer notation in italics with the current version used.

For multiple projects, if there is more than one DAGS Job Number for the project, include all DAGS Job Numbers in the footer.  Do not include the Project Name (etc.) line in the footer.  Use the following format for the specification footer.

TG15595 v03.05	Commissioning of HVAC Systems

Job No.	[00-00-0000]	Page []

[00-00-0000]

#### End Footer Sample

SECTION 15595 - COMMISSIONING OF HVAC SYSTEMS

PART 1 - GENERAL

1.01	SUMMARY

A.	This section covers the commissioning of the air conditioning, ventilation and related systems.  Commissioning is the process of achieving, verifying and documenting the performance of the air conditioning and ventilation system to meet the design intent and functional and operational needs.

SPECIFIER’S NOTE: Describe the air conditioning system pertaining to the project in paragraph 1.01.B.  The following paragraph is an example description.

EXAMPLE:

The air conditioning system main plant consists of two (2) main chillers, a jockey chiller serving off hour/24 hour air conditioning needs, two (2) cooling towers, constant and variable speed chilled water pumps, and three (3) condenser water pumps.  The building’s air conditioning system consists of constant and variable speed air handling units and fan coil units.  Variable air volume (VAV) boxes regulate the air flow into the various spaces.  Exhaust fans ventilate the toilets, mechanical rooms, electrical rooms and the interior parking areas.

1.03	RELATED WORK SPECIFIED IN OTHER SECTIONS

A.	The air conditioning and ventilation system as specified in other sections of DIVISION 15.

B.	Electrical work as specified in DIVISION 16.

1.04	SUBMITTALS

A.	Submit the following in accordance with SECTION 15011 - GENERAL MECHANICAL REQUIREMENTS.

1.	Shop Drawings: None

2.	Product Data: None

3.	Schedules:

(a)	Commissioning Team:  List of team members who will represent the Contractor in the pre-commissioning checks and functional performance testing, at least 2 weeks prior to the start of pre-commissioning checks.  Proposed revision to the list, prior to the start of the impacted work.

(b)	Test Procedures:  Detailed procedures for pre-commissioning checks and functional performance tests, at least 4 weeks prior to the start of pre-commissioning checks.

(c)	Test Schedule:  Schedule for pre-commissioning checks and functional performance tests, at least 2 weeks prior to the start of pre-commissioning checks.

4.	Reports.

(a)	Test Reports:  Completed pre-commissioning checklists and functional performance test checklists organized by system and by subsystem and submitted as one package.  The results of failed tests shall be included along with a description of the corrective action taken.

5.	Certificates of Conformance or Compliance.

6.	As-built Drawings: None

7.	Operations and Maintenance Manuals: None

8.	Guarantee and Certificate:

SPECIFIER’S NOTE: Confirm referenced sections in paragraph 1.05.A.

1.05	SEQUENCING AND SCHEDULING

A.	The work described in this Section shall begin only after all work required in related Sections, including Section 15910 - DIRECT DIGITAL CONTROL SYSTEMS and Section 15990 - TESTING AND BALANCING AIR AND WATER SYSTEMS, has been successfully completed, and all test and inspection reports and operation and maintenance manuals required in these Sections have been submitted and approved.

PART 2   PRODUCTS  [Not Applicable]

PART 3   EXECUTION

3.01	COMMISSIONING TEAM AND CHECKLISTS

A.	The Contractor shall designate team members to participate in the pre-commissioning checks and the functional performance testing specified.  In addition, the State will be represented by the State’s Commissioning Agent, DAGS Inspector, and the Design Agent’s Representative.  The team members are:

1.	Symbol	Function

Q	Contractor’s Chief Quality Control Representative

M	Contractor’s Mechanical Representative

E	Contractor’s Electrical Representative

T	Contractor’s Testing, Adjusting, and Balancing Representative

C	Contractor’s Controls Representative

O	State’s Commissioning Agent

B.	The commissioning team shall complete each checklist in appendices located at the end of this section. Each commissioning team member shall accept of each pre-commissioning checklist item, by initials and date.  Items noted with an “X” (or blacked out) indicates that participation by that individual is not required.  Also, each commissioning team member shall accept each functional performance test checklist by signature and date.

3.02	TESTS

A.	The pre-commissioning checks and functional performance tests shall be performed in a manner which essentially duplicates the checking, testing, and inspection methods established in the related Sections.  Where checking, testing, and inspection methods are not specified in other Sections, methods shall be established which will provide the information required.  Testing and verification required by this Section shall be performed during the Commissioning phase.  Requirements in related Sections are independent from the requirements of this Section and shall not be used to satisfy any of the requirements specified in this Section.  The Contractor shall provide all materials, services, and labor required to perform the pre-commissioning checks and functional performance tests.  A pre-commissioning check or functional performance test shall be aborted if any system deficiency prevents the successful completion of the test or if any participating non-State commissioning team member of which participation is specified is not present for the test.  The Contractor shall reimburse the State for all costs associated with effort lost due to tests that are aborted.  These costs shall include salary, travel costs and per diem (where applicable) for State commissioning team members.

B.	Pre-Commissioning Checks:  Perform for the items indicated on the checklists in Appendix A.  Deficiencies discovered during these checks shall be corrected and retested in accordance with the applicable contract requirements.

C.	Functional Performance Tests:  Perform for the items indicated on the checklists in Appendix B.  Functional performance tests shall begin only after all pre-commissioning checks have been successfully completed.  Tests shall prove all modes of the sequences of operation, and shall verify all other relevant contract requirements.  Tests shall begin with equipment or components and shall progress through subsystems to complete systems.  Upon failure of any functional performance test checklist item, the Contractor shall correct all deficiencies in accordance with the applicable contract requirements.  The checklist shall then be repeated until it has been completed with no errors.

SPECIFIER’S NOTE:  Confirm requirements and modify to suite Project.

3.03	PRE-COMMISSIONING CHECKLISTS [APPENDIX A]

A.	Pre-commissioning checklist for equipment and systems:

| EQUIPMENT / SYSTEM | PRE-COMMISSIONING CHECKLIST |
| --- | --- |
| Chiller Plant | <Required><Not Required> |
| Chilled Water Piping | <Required><Not Required> |
| Condenser Water Piping | <Required><Not Required> |
| Chilled Water Pumps | <Required><Not Required> |
| Chilled Water Pumps With VFD | <Required><Not Required> |
| Condenser Water Pumps | <Required><Not Required> |
| Chillers | <Required><Not Required> |
| Cooling Towers | <Required><Not Required> |
| DDC System | <Required><Not Required> |
| Exhaust Fans | <Required><Not Required> |
| Chemical System | <Required><Not Required> |
| Fan Coil Unit | <Required><Not Required> |
| AHU With VFD | <Required><Not Required> |
| VAV Boxes | <Required><Not Required> [20 Per Floor] |
| Ductwork | <Required><Not Required> |
| DDC System | <Required><Not Required> |

B.	Pre-commissioning Checklist: Piping

For Piping System at Chiller Plant ______________________

| Checklist Items |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Installation | Q | M | E | T | C | O |
|  | a. | Piping complete |  |  |  |  |  |  |
|  | b. | As-built shop drawings submitted |  |  |  |  |  |  |
|  | c. | Piping flushed and cleaned |  |  |  |  |  |  |
|  | d. | Strainers cleaned |  |  |  |  |  |  |
|  | e. | Valves installed as required |  |  |  |  |  |  |
|  | f. | Piping insulated as required |  |  |  |  |  |  |
|  | g. | Thermometers and gauges installed as required |  |  |  |  |  |  |
|  | h. | Verify operation of valves |  |  |  |  |  |  |
|  | i. | Air vents installed as specified |  |  |  |  |  |  |
|  | j. | Flexible connectors installed as specified |  |  |  |  |  |  |
|  | k. | Verify that piping has been labeled and valves identified as specified |  |  |  |  |  |  |
| 2. | Testing, Adjusting, and Balancing (TAB) | Q | M | E | T | C | O |
|  | a. | Hydrostatic test complete |  |  |  |  |  |  |
|  | b. | TAB operation complete |  |  |  |  |  |  |

C.	Pre-commissioning Checklist: Pumps

For Pump  ______________________________________________

| Checklist Items |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Installation | Q | M | E | T | C | O |
|  | a | Pump grouted in place |  |  |  |  |  |  |
|  | b | Pump vibration isolation devices functional |  |  |  |  |  |  |
|  | c | Pump/motor coupling alignment verified |  |  |  |  |  |  |
|  | d | Piping system installed |  |  |  |  |  |  |
|  | e | Piping system pressure tested |  |  |  |  |  |  |
|  | f | Pump not leaking |  |  |  |  |  |  |
|  | g | Field assembled couplings aligned to meet manufacturer's prescribed tolerances |  |  |  |  |  |  |
| 2 | Electrical | Q | M | E | T | C | O |
|  | a | Power available to pump disconnect |  |  |  |  |  |  |
|  | b | Pump rotation verified |  |  |  |  |  |  |
|  | c | Control system interlocks functional |  |  |  |  |  |  |
|  | d | Verify that power disconnect is located within sight of the unit it controls |  |  |  |  |  |  |
|  | e | Variable frequency drive functional |  |  |  |  |  |  |
| 3 | Testing, Adjusting, and Balancing (TAB) | Q | M | E | T | C | O |
|  | a | Pressure/temperature gauges installed |  |  |  |  |  |  |
|  | b | Piping system cleaned |  |  |  |  |  |  |
|  | c | Water balance complete |  |  |  |  |  |  |
|  | d | Water balance with design maximum flow |  |  |  |  |  |  |
|  | e | TAB Report submitted |  |  |  |  |  |  |

D.	Pre-commissioning Checklist – Centrifugal Chiller

For Chiller:  ____________________________________________

| Checklist Items |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Installation | Q | M | E | T | C | O |
|  | a | Chilled water connection properly piped |  |  |  |  |  |  |
|  | b | Condenser water connections properly piped |  |  |  |  |  |  |
|  | c | Chilled water pipe leak tested |  |  |  |  |  |  |
|  | d | Condenser water pipe leak tested |  |  |  |  |  |  |
|  | e | High efficiency purge unit installed and operating as specified |  |  |  |  |  |  |
|  | f | Refrigerant leak detector installed |  |  |  |  |  |  |
|  | g | Oxygen sensor installed and tested |  |  |  |  |  |  |
|  | h | Mechanical room ventilation installed as specified |  |  |  |  |  |  |
|  | i | Manufacturer’s required maintenance clearance provided |  |  |  |  |  |  |
|  | j | Field assembled couplings aligned to meet manufacturer’s prescribed tolerances |  |  |  |  |  |  |
| 2 | Electrical | Q | M | E | T | C | O |
|  | a | Power available to unit starter |  |  |  |  |  |  |
|  | b | Power available to unit control panel |  |  |  |  |  |  |
|  | c | Verify that power disconnect is located within sight of the unit it co |  |  |  |  |  |  |
| 3 | Chiller Controls | Q | M | E | T | C | O |
|  | a | Factory startup, witness tests and checkout complete |  |  |  |  |  |  |
|  | b | Chiller safety/protection devices installed and tested. |  |  |  |  |  |  |
|  | c | Chilled water flow switch installed. |  |  |  |  |  |  |
|  | d | Chilled water flow switch tested. |  |  |  |  |  |  |
|  | e | Chilled water pump interlock installed. |  |  |  |  |  |  |
|  | f | Chilled water pump interlock tested. |  |  |  |  |  |  |
|  | g | Condenser water flow switch installed. |  |  |  |  |  |  |
|  | h | Condenser water flow switch tested. |  |  |  |  |  |  |
|  | i | Condenser water pump interlock installed. |  |  |  |  |  |  |
|  | j | Condenser water pump interlock tested. |  |  |  |  |  |  |

E.	Pre-commissioning - Cooling Tower

For Cooling Tower:  ____________________________________

| Checklist Items |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Installation | Q | M | E | T | C | O |
|  | a | Cooling tower in place. |  |  |  |  |  |  |
|  | b | Cooling tower piped. |  |  |  |  |  |  |
|  | c | Cooling tower fan drive adjusted. |  |  |  |  |  |  |
|  | d | Cooling tower makeup water supply piped and meter installed. |  |  |  |  |  |  |
|  | e | Verify makeup control valve can shutoff. |  |  |  |  |  |  |
|  | f | Fan bearings lubricated and blade pitch adjusted |  |  |  |  |  |  |
|  | g | Manufacturer's required maintenance/operational clearance provided |  |  |  |  |  |  |
| 2 | Electrical | Q | M | E | T | C | O |
|  | a | Power available to tower disconnect switch |  |  |  |  |  |  |
|  | b | Control system interlocks functional |  |  |  |  |  |  |
|  | c | Motor and fan rotation checked |  |  |  |  |  |  |
|  | d | Verify that power disconnect is located within sight of the unit’s controls |  |  |  |  |  |  |
| 3 | Piping | Q | M | E | T | C | O |
|  | a | Tower basin is clean and filled |  |  |  |  |  |  |
|  | b | Condenser water treatment functional |  |  |  |  |  |  |
|  | c | Water balance with design flow verified |  |  |  |  |  |  |
|  | d | Water distribution headers balanced |  |  |  |  |  |  |

F.	Pre-commissioning - Fan Coiling Unit

For Fan coil Unit:  ____________________________________

| Checklist Items |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Installation | Q | M | E | T | C | O |
|  | a | Vibration isolation devices installed |  |  |  |  |  |  |
|  | b | Access doors/removable panels are operable and sealed |  |  |  |  |  |  |
|  | c | Casing undamaged |  |  |  |  |  |  |
|  | d | Insulation undamaged |  |  |  |  |  |  |
|  | e | Condensate drainage is unobstructed |  |  |  |  |  |  |
|  | f | Fan belt adjusted |  |  |  |  |  |  |
|  | g | Any damage to coil fins has been repaired |  |  |  |  |  |  |
|  | h | Manufacturer's required maintenance clearance provided |  |  |  |  |  |  |
| 2 | Electrical | Q | M | E | T | C | O |
|  | a | Power available to unit disconnect |  |  |  |  |  |  |
|  | b | Power available to unit control panel |  |  |  |  |  |  |
|  | c | Proper motor rotation verified |  |  |  |  |  |  |
|  | d | Verify that power disconnect is located within sight of the unit’s controls |  |  |  |  |  |  |
| 3 | Coils | Q | M | E | T | C | O |
|  | a | Chilled water piping properly connected |  |  |  |  |  |  |
|  | b | Chilled water piping pressure tested |  |  |  |  |  |  |
|  | c | Condensate piping properly connected |  |  |  |  |  |  |
|  | d | Condensate piping leak tested |  |  |  |  |  |  |
|  | e | Air vents installed on water coils with shutoff valves as specified |  |  |  |  |  |  |
|  | f | Any damage to coil fins have been repaired |  |  |  |  |  |  |
| 4 | Controls | Q | M | E | T | C | O |
|  | a | Control valves/actuators properly installed |  |  |  |  |  |  |
|  | b | Control valves/actuators operable |  |  |  |  |  |  |
|  | c | Verify proper location and installation of thermostat |  |  |  |  |  |  |
| 5 | Testing, Adjusting and Balancing (TAB) | Q | M | E | T | C | O |
|  | a | Construction filters removed and replaced |  |  |  |  |  |  |
|  | b | TAB results +10%/_0% of cfm shown on drawings |  |  |  |  |  |  |
|  | c | TAB Report submitted |  |  |  |  |  |  |

G.	Pre-commissioning – Air Handling Unit

For Air handling Unit:  ____________________________________

| Checklist Items |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Installation | Q | M | E | T | C | O |
|  | a | Vibration isolation devices installed |  |  |  |  |  |  |
|  | b | Access doors/removable panels are operable and sealed |  |  |  |  |  |  |
|  | c | Casing undamaged |  |  |  |  |  |  |
|  | d | Insulation undamaged |  |  |  |  |  |  |
|  | e | Condensate drainage is unobstructed. (Visually verify drainage by pouring a cup of water into drain pan.) |  |  |  |  |  |  |
|  | f | Fan belt adjusted |  |  |  |  |  |  |
|  | g | Any damage to coil fins has been repaired |  |  |  |  |  |  |
|  | h | Manufacturer’s required maintenance clearance provided |  |  |  |  |  |  |
|  | i | Ductwork complete |  |  |  |  |  |  |
|  | j | Ductwork leak test complete |  |  |  |  |  |  |
|  | k | Fire dampers, smoke dampers and access doors installed as required |  |  |  |  |  |  |
|  | l | Ductwork insulated as required |  |  |  |  |  |  |
|  | m | Thermometers and gauges installed as required |  |  |  |  |  |  |
|  | n | Verify open/closed status of dampers |  |  |  |  |  |  |
|  | o | Verify smoke dampers operation |  |  |  |  |  |  |
|  | p | Flexible connectors installed as specified |  |  |  |  |  |  |
| 2 | Electrical | Q | M | E | T | C | O |
|  | a | Power available to unit disconnect |  |  |  |  |  |  |
|  | b | Power available to unit control panel |  |  |  |  |  |  |
|  | c | Proper motor rotation verified |  |  |  |  |  |  |
|  | d | Verify that power disconnect is located within sight of the unit’s controls |  |  |  |  |  |  |
| 3 | Coils | Q | M | E | T | C | O |
|  | a | Chilled water piping properly connected |  |  |  |  |  |  |
|  | b | Chilled water piping pressure tested |  |  |  |  |  |  |
|  | c | Condensate piping properly connected |  |  |  |  |  |  |
|  | d | Condensate piping leak tested |  |  |  |  |  |  |
|  | e | Air vents installed on water coils with shutoff valves as specified |  |  |  |  |  |  |
|  | f | Any damage to coil fins have been repaired |  |  |  |  |  |  |
| 4 | Controls | Q | M | E | T | C | O |
|  | a | Control valves/actuators properly installed |  |  |  |  |  |  |
|  | b | Control valves/actuators operable |  |  |  |  |  |  |
|  | c | Dampers/actuators properly installed |  |  |  |  |  |  |
|  | d | Dampers/actuators operable |  |  |  |  |  |  |
|  | e | Verify proper location and installation of thermostat |  |  |  |  |  |  |
| 5 | Testing, Adjusting and Balancing (TAB) | Q | M | E | T | C | O |
|  | a | Construction filters removed and replaced |  |  |  |  |  |  |
|  | b | TAB results +10%/_0% of cfm shown on drawings |  |  |  |  |  |  |
|  | c | TAB Report submitted |  |  |  |  |  |  |

H.	Pre-commissioning – Variable Volume Air Handling Unit

For Air handling Unit:  ____________________________________

| Checklist Items |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Installation | Q | M | E | T | C | O |
|  | a | Vibration isolation devices installed |  |  |  |  |  |  |
|  | b | Access doors/removable panels are operable and sealed |  |  |  |  |  |  |
|  | c | Casing undamaged |  |  |  |  |  |  |
|  | d | Insulation undamaged |  |  |  |  |  |  |
|  | e | Condensate drainage is unobstructed. (Visually verify drainage by pouring a cup of water into drain pan.) |  |  |  |  |  |  |
|  | f | Fan belt adjusted |  |  |  |  |  |  |
|  | g | Any damage to coil fins has been repaired |  |  |  |  |  |  |
|  | h | Manufacturer’s required maintenance clearance provided |  |  |  |  |  |  |
|  | i | Ductwork complete |  |  |  |  |  |  |
|  | j | Ductwork leak test complete |  |  |  |  |  |  |
|  | k | Fire dampers, smoke dampers and access doors installed as required |  |  |  |  |  |  |
|  | l | Ductwork insulated as required |  |  |  |  |  |  |
|  | m | Theromometers and gauges installed as required |  |  |  |  |  |  |
|  | n | Verify open/closed status of dampers |  |  |  |  |  |  |
|  | o | Verify smoke dampers operation |  |  |  |  |  |  |
|  | p | Flexible connectors installed as specified |  |  |  |  |  |  |
| 2 | Electrical | Q | M | E | T | C | O |
|  | a | Power available to unit disconnect |  |  |  |  |  |  |
|  | b | Power available to unit control panel |  |  |  |  |  |  |
|  | c | Proper motor rotation verified |  |  |  |  |  |  |
|  | d | Verify that power disconnect is located within sight of the unit’s controls |  |  |  |  |  |  |
| 3 | Coils | Q | M | E | T | C | O |
|  | a | Chilled water piping properly connected |  |  |  |  |  |  |
|  | b | Chilled water piping pressure tested |  |  |  |  |  |  |
|  | c | Condensate piping properly connected |  |  |  |  |  |  |
|  | d | Condensate piping leak tested |  |  |  |  |  |  |
|  | e | Air vents installed on water coils with shutoff valves as specified |  |  |  |  |  |  |
|  | f | Any damage to coil fins have been repaired |  |  |  |  |  |  |
| 4 | Controls | Q | M | E | T | C | O |
|  | a | Control valves/actuators properly installed |  |  |  |  |  |  |
|  | b | Control valves/actuators operable |  |  |  |  |  |  |
|  | c | Dampers/actuators properly installed |  |  |  |  |  |  |
|  | d | Dampers/actuators operable |  |  |  |  |  |  |
|  | e | Verify proper location and installation of thermostat |  |  |  |  |  |  |
|  | f | Verify proper location, installation and calibration of duct static pressure sensor |  |  |  |  |  |  |
|  | g | Fan air volume controller operable |  |  |  |  |  |  |
|  | h | Air handler controls system operational |  |  |  |  |  |  |
| 5 | Testing, Adjusting and Balancing (TAB) | Q | M | E | T | C | O |
|  | a | Construction filters removed and replaced |  |  |  |  |  |  |
|  | b | TAB results +10%/_0% of cfm shown on drawings |  |  |  |  |  |  |
|  | c | TAB Report submitted |  |  |  |  |  |  |
|  | d | TAB results for outside air intake within +10%/_0% of both the minimum and maximum cfm shown on drawings |  |  |  |  |  |  |

I.	Pre-commissioning – Ductwork

For Air handling Unit:  ____________________________________

| Checklist Items |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Installation | Q | M | E | T | C | O |
|  | a | Ductwork Complete |  |  |  |  |  |  |
|  | b | As-built shop drawings submitted |  |  |  |  |  |  |
|  | c | Ductwork leak test complete |  |  |  |  |  |  |
|  | d | Fire dampers, smoke dampers and access doors installed as required |  |  |  |  |  |  |
|  | e | Ductwork insulated as required |  |  |  |  |  |  |
|  | f | Verify open/closed status of dampers |  |  |  |  |  |  |
|  | g | Verify smoke dampers operation |  |  |  |  |  |  |
|  | h | Flexible connectors installed as specified |  |  |  |  |  |  |
| 2 | Testing, Adjusting and Balancing (TAB) | Q | M | E | T | C | O |
|  | a | TAB Report submitted |  |  |  |  |  |  |

J.	Pre-commissioning – VAV Terminal

For VAV Terminalt:  _______________________________________

| Checklist Items |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Installation | Q | M | E | T | C | O |
|  | a | VAV terminal in place. |  |  |  |  |  |  |
|  | b | VAV terminal ducted. |  |  |  |  |  |  |
|  | c | VAV terminal connected to controls. |  |  |  |  |  |  |
|  | d | Manufacturer’s required maintenance clearance provided. |  |  |  |  |  |  |
| 2 | Controls | Q | M | E | T | C | O |
|  | a | Cooling only VAV terminal controls set. |  |  |  |  |  |  |
|  | b | Cooling only VAV controls verified. |  |  |  |  |  |  |
| 3 | Testing, Adjusting and Balancing (TAB) | Q | M | E | T | C | O |
|  | a | Verify terminal maximum airflow set. |  |  |  |  |  |  |
|  | b | Verify terminal minimum airflow set. |  |  |  |  |  |  |
|  | c | TAB operation complete. |  |  |  |  |  |  |

K.	Pre-commissioning – Exhaust Fan

For Exhaust Fan:  _________________________________________

| Checklist Items |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Installation | Q | M | E | T | C | O |
|  | a | Vibration isolation devices installed. |  |  |  |  |  |  |
|  | b | Casing undamaged. |  |  |  |  |  |  |
|  | c | Fan belt adjusted. |  |  |  |  |  |  |
|  | d | Manufacturer's required maintenance clearance provided. |  |  |  |  |  |  |
|  | e | Ductwork complete. |  |  |  |  |  |  |
|  | f | Ductwork leak test complete. |  |  |  |  |  |  |
|  | g | Fire dampers, smoke dampers and access doors installed as required. |  |  |  |  |  |  |
|  | h | Verify open/closed status of dampers. |  |  |  |  |  |  |
|  | i | Verify smoke dampers operation. |  |  |  |  |  |  |
|  | j | Flexible connectors installed as specified. |  |  |  |  |  |  |
| 2 | Electrical | Q | M | E | T | C | O |
|  | a | Power available to unit disconnect switch. |  |  |  |  |  |  |
|  | b | Proper motor rotation verified. |  |  |  |  |  |  |
|  | c | Verify that power disconnect is located within sight of the unit’s controls. |  |  |  |  |  |  |
| 3 | Controls | Q | M | E | T | C | O |
|  | a | Control interlocks properly installed. |  |  |  |  |  |  |
|  | b | Control interlocks operable. |  |  |  |  |  |  |
|  | c | Dampers/actuators properly installed. |  |  |  |  |  |  |
|  | d | Dampers/actuators operable. |  |  |  |  |  |  |
|  | e | Verify proper location and installation of thermostat. |  |  |  |  |  |  |
| 5 | Testing, Adjusting and Balancing (TAB) | Q | M | E | T | C | O |
|  | a | TAB results +10%/_0% of cfm shown on drawings. |  |  |  |  |  |  |
|  | b | TAB Report submitted. |  |  |  |  |  |  |

L.	Pre-commissioning – DCC System

For DCC System:  _________________________________________

| Checklist Items |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Installation | Q | M | E | T | C | O |
|  | a | Asbuilt shop drawings submitted. |  |  |  |  |  |  |
|  | b | Layout of control panel matches drawings. |  |  |  |  |  |  |
|  | c | Framed instructions mounted in or near control panel. |  |  |  |  |  |  |
|  | d | Components properly labeled on inside and outside of panel. |  |  |  |  |  |  |
|  | e | Control components piped and/or wired to each labeled terminal strip. |  |  |  |  |  |  |
|  | f | DDC system connection made to each labeled terminal strip as shown. |  |  |  |  |  |  |
|  | g | Control wiring and tubing labeled at all terminations, splices, and junctions. |  |  |  |  |  |  |
|  | h | Shielded wiring used on electronic sensors. |  |  |  |  |  |  |
|  | i | Programming/ graphics complete. |  |  |  |  |  |  |
| 2 | Electrical | Q | M | E | T | C | O |
|  | a | 110 volt AC power available to panel. |  |  |  |  |  |  |
| 3 | Testing, Adjusting and Balancing (TAB) | Q | M | E | T | C | O |
|  | a | TAB Report submitted. |  |  |  |  |  |  |

3.04	FUNCTIONAL PERFORMANCE TEST CHECKLISTS [APPENDIX B]

A.	Provide functional performance checklist for equipment and systems:

| EQUIPMENT / SYSTEM | PERFORMANCE CHECKLIST |
| --- | --- |
| Chiller Plant | <Required><Not Required> |
| Chilled Water Piping | <Required><Not Required> |
| Condenser Water Piping | <Required><Not Required> |
| Chilled Water Pumps | <Required><Not Required> |
| Chilled Water Pumps With VFD | <Required><Not Required> |
| Condenser Water Pumps | <Required><Not Required> |
| Chillers | <Required><Not Required> |
| Cooling Towers | <Required><Not Required> |
| DDC System | <Required><Not Required> |
| Exhaust Fans | <Required><Not Required> |
| Chemical System | <Required><Not Required> |
| Fan Coil Unit | <Required><Not Required> |
| AHU With VFD | <Required><Not Required> |
| VAV Boxes | <Required><Not Required> [20 Per Floor] |
| Ductwork | <Required><Not Required> |
| DDC System | <Required><Not Required> |

B.	Functional Performance Test – Pumps

For Pumps:  _________________________________________

Prior to performing these checks, ensure that for closed loop systems, system is pressurized and the make-up water system is operational or, for open loop systems, that the sumps are filled to the proper level.

| 1. | Energize and de-energize pump start using control system commands (all possible combinations, on/auto, etc.). Verify pump starts and stops as expected. |
| --- | --- |
|  |  |  |  |  | ON |  | OFF |
|  | Manual switch: |  |  |  |  |  |  |
|  | AUTO Start/Stop: | Initiating device |  |  |  |
|  | a. Record Pressure drop across strainer: |
|  | Strainer inlet pressure |  |  |  | psig |
|  | Strainer outlet pressure |  |  |  | psig |
|  | Strainer differential pressure |  |  |  | psig |
|  | b. Annotate pump inlet/outlet design conditions and compare to Testing, Adjusting and Balancing report (TAB) |
|  |  | Design |  | TAB |
|  | Pump inlet pressure (psig) |  |  |  |
|  | Pump outlet pressure (psig) |  |  |  |
|  | PUMP FLOW RATE (gpm) |  |  |  |
|  | c. Operate pump at shutoff and at 100 percent of design flow when all components are in full flow. Plot test readings on pump curve and compare results against readings taken from flow measuring devices. |
|  |  | Shutoff |  | 100 Percent |
|  | Pump inlet pressure (psig) |  |  |  |
|  | Pump outlet pressure (psig) |  |  |  |
|  | Pump flow rate, from flow measuring device (gpm) |  |  |  |
|  | Pump flow rate, from pump curve (gpm) |  |  |  |
|  | d. For variable speed pumps, operate pump at 50% of design flow and at minimum flow or when all components are in full by-pass. Plot test readings on pump curve and compare results against readings taken from flow measuring devices. |
|  |  | 50% flow |  | Minimum flow |
|  | Pump inlet pressure (psig) |  |  |  |
|  | Pump outlet pressure (psig) |  |  |  |
|  | Pump flow rate, from flow measuring device (gpm) |  |  |  |
|  | Pump flow rate, from pump curve (gpm) |  |  |  |
| 2. | Verify motor amperage each phase and voltage phase to phase and phase to ground for both the full flow and the minimum flow conditions. |
|  | a. Full flow: | Phase 1 |  | Phase 2 |  | Phase 3 |
|  | Amperage |  |  |  |  |  |
|  | Voltage |  |  |  |  |  |
|  | Voltage to Ground |  |  |  |  |  |
|  | b. Minimum Flow: | Phase 1 |  | Phase 2 |  | Phase 3 |
|  | Amperage |  |  |  |  |  |
|  | Voltage |  |  |  |  |  |
|  | Voltage to Ground |  |  |  |  |  |
| 3. | Unusual vibration, noise, and other similar items. |
| 4. | Certification: We the undersigned have witnessed the above functional performance tests and certify that the item tested has met the performance requirements in this section of the specifications. |
|  |  | Signature | Date |
|  | Contractor’s Chief Quality Control Representative | _____________________ | _________ |
|  | Contractor’s Mechanical Representative | _____________________ | _________ |
|  | Contractor’s Electrical Representative | _____________________ | _________ |
|  | Contractor's Testing, Adjusting and Balancing Representative | _____________________ | _________ |
|  | Contractor’s Controls Representative | _____________________ | _________ |
|  | State’s Commissioning Agent Representative | _____________________ | _________ |

C.	Functional Performance Test – Centrifugal Chiller

For Chiller:  _________________________________________

| 1. | Functional Performance Test: Contractor shall demonstrate operation of chilled water system as per specifications including the following: |
| --- | --- |
|  | a. Start all the building’s AHU’s to provide maximum load for the chiller. Set each AHU control valve to full cooling. |
|  |  | AHU No |  | Design Load (BTU) |  | AHU |  | Design Load (BTU) |
|  | b. Time of day startup program initiates chiller start sequence (start initiated by entering start time in startup program): |  | Satisfactory |
|  | c. Start condenser water pump and establish condenser water flow. Verify condenser water proof-of-flow switch operation allows chiller startup. |  | Satisfactory |
|  | d. Start primary chilled water pump and establish chilled water flow. Verify chilled water proof-of-flow switch operation allows chiller startup. |  | Satisfactory |
|  | e. Verify chiller control system energizes chiller start sequence. Record time of day startup initiated and time of day compressor starts. Check against chiller startup instructions from manufacturer. |  | Satisfactory |
|  |  | Compressor Amps |
|  | Time Start-up initiated |  |  |  |  |  |  |  |
|  | Time Compressor starts |  |  |  |  |  |  |  |
|  | f. Verify chiller senses chilled water temperature above set point and chiller control system activates chiller start. |
|  | Chilled water return temperature |  |  |  |
|  | Chilled water supply temperature |  |  |  |
|  | Chilled water set point temperature |  |  |  |
|  | g. Verify functioning of “soft start” sequence. |
|  | Set point of VFD acceleration |  |  |
|  | Record actual time from start to constant speed |  |  |
|  | Final compressor rpm |  |  |
|  | Record peak amps during start up: |  |  |  |  |  |
|  | h. Shut off air handling equipment to remove load on chilled water system. Verify chiller shutdown sequence is initiated and accomplished after load is removed. |  |  |
|  | i. Restart air-handling equipment one minute after chiller shut down. |
|  | Record time compressor reaches 0 rpm. |  |  |
|  | Record time AHU restarted. |  |  |
|  | j. Verify condenser water pump, cooling tower, and chiller restart sequence. |
|  | Condenser water pump starts satisfactory |  |  |
|  | Chilled water pump starts satisfactory |  |  |
|  | Cooling tower fan starts satisfactory |  |  |
|  | Chiller starts satisfactory |  |  |
| 2. | Certification: We the undersigned have witnessed the above functional performance tests and certify that the item tested has met the performance requirements in this section of the specifications. |
|  |  | Signature | Date |
|  | Contractor’s Chief Quality Control Representative | _____________________ | _________ |
|  | Contractor’s Mechanical Representative | _____________________ | _________ |
|  | Contractor’s Electrical Representative | _____________________ | _________ |
|  | Contractor’s Testing, Adjusting and Balancing Representative | _____________________ | _________ |
|  | Contractor’s Controls Representative | _____________________ | _________ |
|  | State’s Commissioning Agent Representative | _____________________ | _________ |

D.	Functional Performance Test – Cooling Tower

For Cooling Tower:  _______________________________________

| 1. | Functional Performance Test: Contractor shall demonstrate operation of cooling tower as per specifications and the following: |
| --- | --- |
|  | a. Activate cooling tower fan start using control system command through DDC system. This should first start condenser water pump, establish flow and starting of the fan start if the condenser water temperature exceeds the set point |
|  | Fan Motor Amps |  |  |  |  |  |  |
|  | Condenser Supply Water temperature In Degrees F: | Set point |  | Test |
|  | b. Verify makeup water float valve is functioning at level set point and overflow drain is free flowing: |  |  |
|  | c. Activate chemical treatment feed valve, verify makeup of chemical treatment system, pump, and controls are operational. |
|  | Record conductivity. |  |  |
|  | Check solenoid valve for bleed off is operational. |  |  |
|  | Record set point for chemical addition (i.e. time or conductivity level) |  |  |
|  | d. Entering condenser water temperature: |  | °F |
|  | e. Leaving condenser water temperature: |  | °F |
|  | f. Air volume measured: |  | cfm |
|  | g. Air volume calculated: |  | cfm |
|  | h. Entering dry/wet bulb temperature: |  | / |  | °F |
|  | i. Leaving dry/wet bulb temperature: |  | / |  | °F |
|  | j. Measured condenser water flow: |  | gpm |
| 2. | Certification: We the undersigned have witnessed the above functional performance tests and certify that the item tested has met the performance requirements in this section of the specifications. |
|  |  | Signature | Date |
|  | Contractor’s Chief Quality Control Representative | _____________________ | _________ |
|  | Contractor’s Mechanical Representative | _____________________ | _________ |
|  | Contractor’s Electrical Representative | _____________________ | _________ |
|  | Contractor's Testing, Adjusting and Balancing Representative | _____________________ | _________ |
|  | Contractor’s Controls Representative | _____________________ | _________ |
|  | State’s Commissioning Agent Representative | _____________________ | _________ |

E.	Functional Performance Test – VAV Terminals

The Commissioning Agent will select the VAV terminals to be spot-checked during the functional performance test.  The number of terminals shall not exceed [10] per floor.

| 1. | Functional Performance Test: Contractor shall demonstrate operation of selected VAV boxes as per specifications and the following: |
| --- | --- |
|  | a. Cooling only VAV boxes: |
|  | Verify VAV box responds to room temperature set point adjustment. Turn thermostat to 5°F above ambient and measure maximum airflow. Turn thermostat to 5°F below ambient and measure minimum airflow. |
|  |  | VAV Box | Minimum CFM | Maximum CFM |
|  |  |  | Tab Report | Test | Tab Report | Test |
|  | Check Damper maximum/minimum flow settings: |
|  |  | VAV Box | Minimum CFM | Maximum CFM |
|  |  |  | Tab Report | Test | Tab Report | Test |
| 2. | Certification: We the undersigned have witnessed the above functional performance tests and certify that the item tested has met the performance requirements in this section of the specifications. |
|  |  | Signature | Date |
|  | Contractor’s Chief Quality Control Representative | _____________________ | _________ |
|  | Contractor’s Mechanical Representative | _____________________ | _________ |
|  | Contractor’s Electrical Representative | _____________________ | _________ |
|  | Contractor's Testing, Adjusting and Balancing Representative | _____________________ | _________ |
|  | Contractor’s Controls Representative | _____________________ | _________ |
|  | State’s Commissioning Agent Representative | _____________________ | _________ |

F.	Functional Performance Test – Variable Volume Air Handling Unit

For Air Handling Unit:  ___________________________________

| 1. | Functional Performance Test: Contractor shall demonstrate operation of air handling unit as per specifications including the following: |
| --- | --- |
|  | a. The following shall be verified when the supply fan operating mode is initiated: |
|  | 1) All valves in normal position. Set point equals |  | °F |
|  | Record supply air temperature using installed temperature sensor |  | °F |
|  | Record supply air temperature using separate test gauge within 5 feet of the installed sensor |  | °F |
|  | 2) VAV fan VFD controller shall “soft-start” fan |  |
|  | Final fan speed |  |
|  | Time of acceleration to operating speed |  |
|  | 3) Modulate all VAV boxes to minimum air flow and verify that the static pressure does not exceed the design static pressure Class shown. |
|  | Duct Pressure class upstream of VAV boxes: |  | "w.g |
|  | Duct Static pressure at minimum air flow: (Use installed static pressure controller) |  | "w.g |
|  | Duct Static pressure at minimum air flow: (Use test static pressure gauge) |  | "w.g |
|  | b. Occupied mode of operation. |
|  | 1) Exhaust fans energized. |  |
|  | 2) Verify chilled water control valve modulating to maintain leaving air temperature set point by varying set point. |  |
|  | 3) Verify VFD fan controller receiving signal from duct static pressure sensor and modulating fan to maintain supply duct static pressure set point. |  |
|  |  |  | CFM |  | Signal |  | Fan RPM |
|  | 50% of full speed |  |  |  |  |  |
|  | 100% speed |  |  |  |  |  |
|  | c. The following shall be verified when the supply fan off mode is initiated: |
|  | 1) All valves in normal position. |  |  |
|  | 2) Fan de-energizes and fan speed goes to zero. |  |  |
|  | d. Verify the chilled water coil control valve operation by setting all VAV’s to maximum and minimum cooling. |
|  |  | Maximum Cooling | Minimum Cooling |
|  | Supply air volume | cfm |  |  |  |
|  | Supply air temp | °F |  |  |  |
|  | VFD | rpm |  |  |  |
|  | e. Verify safety shut down initiated by duct smoke detectors. |  |
| 2. | Certification: We the undersigned have witnessed the above functional performance tests and certify that the item tested has met the performance requirements in this section of the specifications. |
|  |  | Signature | Date |
|  | Contractor’s Chief Quality Control Representative | _____________________ | _________ |
|  | Contractor’s Mechanical Representative | _____________________ | _________ |
|  | Contractor’s Electrical Representative | _____________________ | _________ |
|  | Contractor's Testing, Adjusting and Balancing Representative | _____________________ | _________ |
|  | Contractor’s Controls Representative | _____________________ | _________ |
|  | State’s Commissioning Agent Representative | _____________________ | _________ |

G.	Functional Performance Test – Fan coil Unit

| 1. | Functional Performance Test: Contractor shall demonstrate operation of selected fan coils as per specifications including the following: |
| --- | --- |
|  | a. Cooling only fan coils: |
|  | 1) Verify fan coil unit response to room temperature set point adjustment. Changes to be cooling set point to cooling set point minus 10°F and return to cooling set point. |  |  |
|  | 2) Check blower fan air flow at each speed |  | cfm |
|  | 3) Check cooling coil water flow |  | gpm |
|  | 4) Verify proper operation of cooling water control valve |  |  |
|  | b. Cooling fan coils: |  |
|  | 1) Verify fan coil unit responds to room temperature set point adjustment |  |  |
|  | 2) Check blower fan airflow. |  | cfm |
|  | 3) Check cooling coil water flow |  | gpm |
|  | 4) Verify proper operation of cooling water control valve by observing the valve movement when the set point has been changed for the test |  |  |
|  | 5) Check cooling mode inlet air temperature |  | °F |
|  | 6) Check cooling mode outlet air temperature |  | °F |
| 2. | Certification: We the undersigned have witnessed the above functional performance tests and certify that the item tested has met the performance requirements in this section of the specifications. |
|  |  | Signature | Date |
|  | Contractor’s Chief Quality Control Representative | _____________________ | _________ |
|  | Contractor’s Mechanical Representative | _____________________ | _________ |
|  | Contractor’s Electrical Representative | _____________________ | _________ |
|  | Contractor's Testing, Adjusting and Balancing Representative | _____________________ | _________ |
|  | Contractor’s Controls Representative | _____________________ | _________ |
|  | State’s Commissioning Agent Representative | _____________________ | _________ |

H.	Functional Performance Test – HVAC DDC System

For HVAC DDC System:  ___________________________________

The Commissioning Agent will select the number of points from the HVAC control systems to undergo functional performance testing. The number of terminals shall not exceed [10%] of the total shown on the points list

| 1. | Functional Performance Test: Contractor shall demonstrate operation of the HVAC controls by performing the following tests and measurements: |
| --- | --- |
|  | a. Verify that controller is maintaining the set point by manually measuring the controlled variable with a thermometer, sling psychrometer, inclined manometer, etc. or other calibrated device or meter that does not rely on the DDC system for the reading. |
|  | b. Verify sensor and controller combination by manually measuring the controlled medium using a separate device from the permanently installed system device. Take readings from control panel display or the equivalent readings from a remote lap top computer and compare readings taken manually. Take reading from the sensor that supplies the reading to the system and convert to the variable being displayed. Record all readings. |
|  |  | Point | Sensor Reading | Manual Measurement | Panel Reading |
|  | c. Verify system stability by changing the control variable set point as follows: |
|  | 1) Air temperature-10°F |  |  |
|  | 2) Water temperature-10°F |  |  |
|  | 3) Static pressure-10% of set point |  |  |
|  | The control system shall be observed for 10 minutes after the change in set point. Instability or excessive hunting will be unacceptable. Report findings. |
|  | d. Verify interlock with other HVAC controls such as exhaust fan and supply fan interlocks. |
|  | e. Verify interlock with fire alarm control panel. |
|  | f. Change controller set point by 10 percent with the DDC system or remote lap top computer and verify the system responds correctly |
| 2. | Verify that the operation of the DDC system conforms to that specified in the sequence of operation for start-up, shutdown and load variations. |
| 3. | Certification: We the undersigned have witnessed the above functional performance tests and certify that the item tested has met the performance requirements in this section of the specifications. |
|  |  | Signature | Date |
|  | Contractor’s Chief Quality Control Representative | _____________________ | _________ |
|  | Contractor’s Mechanical Representative | _____________________ | _________ |
|  | Contractor’s Electrical Representative | _____________________ | _________ |
|  | Contractor's Testing, Adjusting and Balancing Representative | _____________________ | _________ |
|  | Contractor’s Controls Representative | _____________________ | _________ |
|  | State’s Commissioning Agent Representative | _____________________ | _________ |

END OF SECTION 15995